## Sheet1
ANNUAL FIRE PUMP SERVICE TEST DATA
David's Fire Equipment
800-264-0017
Department Name |  |  |  |  | Date
Unit Designation |  |  | Make |  | Model Year
Pump Make | Waterous |  | Model | CM | Serial Number
Rated Capacities |  | 1251 | at 150 PSI (100%)
|  | 882 | at 200 PSI (70%)
|  | 633 | at 250 PSI (50%)
Test Location | Oliver's Pond |  | Temperature | 65F | Elevation | 347
Suction Lift | 5 Feet 5 Inches |  | Suction Hose | (2) 6" x 10'
Vacuum Test
Time to Prime | 11 Sec Pass | XXX | Fail |  | Total Drop | 10 | in/Hg
100% Capacity Test (20 Minutes)
Hose Layout | (3) 3" x 100' Double Jacket Fire Hose |  |  |  | Tip Size | 2-1/4"
| Time | RPM | GPM | Pitot PSI | Pump PSI (Adj)
| 10:15 | 1600 | 1258 | 70 | 150
| 10:20 | 1625 | 1271 | 72 | 150
| 10:25 | 1625 | 1271 | 72 | 150
| 10:30 | 1625 | 1271 | 72 | 150
| 10:35 | 1625 | 1271 | 72 | 150
| Pass/Fail | PASS
70% Capacity Test (10 Minutes)
Hose Layout | (2) 3" X 100' Double Jacket Fire Hose |  |  |  | Tip Size | 1-3/4"
| Time | RPM | GPM | Pitot PSI | Pump PSI (Adj)
| 10:45 | 1780 | 887 | 98 | 200
| 10:50 | 1780 | 887 | 98 | 200
| 10:55 | 1800 | 894 | 100 | 200
| Pass/Fail | PASS
50% Capacity Test (10 Minutes)
Hose Layout | (1) 3" x 100' Double Jacket Fire Hose |  |  |  | Tip Size | 1-1/2"
| Time | RPM | GPM | Pitot PSI | Pump PSI (Adj)
| 11:02 | 1600 | 637 | 96 | 250
| 11:07 | 1580 | 637 | 96 | 250
| 11:12 | 1580 | 637 | 96 | 250
| Pass/Fail | PASS
Test Performed By